## LEE METHOD
LEE METHOD
INPUTS
Voltage | 33 | kV
Fault Current (Ibf) | 10.27 | kA
Gaps B/W Conductors G | 305 | mm
Working Distance D | 457 | mm
FCT in Secs | 0.07 | s
Final Incident Energy
IE= | 243.3153 | J/cm2
| 58.1524 | Cal/cm2
Final Arc Flash Boundary
AFB= | 3187.9826 | mm
| 3.188 | m

## MV- 2018
Step 1: Determine the intermediate arcing currents using the equations provided in section 4.3
Table-1
Arc Flash Calculation 1584 -2018 | [5 empty] | VCB
[6 empty] | 0.6 kV | 2.7 kV | 14.3 kV
Voltage | 13.8 | kV |  |  | K1 | -0.04287 | 0.0065 | 0.005795
Ibf | 5.914 | kA |  |  | K2 | 1.035 | 1.001 | 1.015
Gap B/w Conductors G | 152 | mm |  |  | K3 | -0.083 | -0.024 | -0.011
Working Distance | 914.4 | mm |  |  | K4 | 0 | -1.557e-12 | -1.557e-12
Enclose dimensions |  |  |  |  | K5 | 0 | 4.556e-10 | 4.556e-10
Width | 762 | mm | 508mm to 1244.6mm |  | K6 | -4.783e-09 | -4.186e-08 | -4.186e-08
Height | 1143 | mm | 508mm to 1244.6mm |  | K7 | 1.962e-06 | 8.346e-07 | 8.346e-07
[5 empty] | K8 | -0.000229 | 5.482e-05 | 5.482e-05
[5 empty] | K9 | 0.003141 | -0.003191 | -0.003191
[5 empty] | K10 | 1.092 | 0.9729 | 0.9729
Iarc at 0.6 kV | 4.1447 | kA
Iarc at 2.7 kV | 5.0966 | kA
Iarc at 14.3 kV | 5.5686 | kA
Step 2: Find the final arcing current per the equations and instructions provided in 4.8
Iarc_1 | 10.1278 | kA
Iarc_2 | 5.5482 | kA | 2.7kV Above
Iarc_3 | -18.6579 | kA | 0.6kV to 2.7 kV
Final Iarc | 5.5482 | kA
FCT | 332 | ms
Step 3: Find the final arcing current per the equations and instructions provided in 4.7
Table-6
|  |  | Width< 508 (mm) | 508< Width< 660.4 (mm) | 660 < Width< 1244.6 (mm) | Width>1244.6 (mm)
Width 1 | 29.56 |  | 508 | 660.4 | 1244.6 | 1245
|  |  | 20 | 29.9999 | 29.56 | 46.47
|  |  | Height< 508 (mm) | 508< Height< 660.4 (mm) | 660 < Height< 1244.6 (mm) | Height>1244.6 (mm)
Height 1 | 44.9999 |  | 508 | 660.4 | 1244.6 | 1245
|  |  | 20 | 44.9999 | 44.9999 | 49
Table-7
ESS | 37.28 |  |  | B1 | B2 | B3
|  |  |  | -0.000302 | 0.03441 | 0.4325
Correction factor
CF | 1.2956
Step 4: The intermediate values of incident energy can be found per 4.5
Table-3
[5 empty] | 0.6 kV | 2.7 kV | 14.3 kV
E at 0.6 | 5.8802 | J/cm2 |  | k1 | 0.75336 | 2.4002 | 3.8259
E at 2.7 | 8.5793 | J/cm2 |  | k2 | 0.566 | 0.165 | 0.11
E at 14.3 | 9.6594 | J/cm2 |  | k3 | 1.7526 | 0.3542 | -0.99975
|  |  |  | k4 | 0 | -1.557e-12 | -1.557e-12
|  |  |  | k5 | 0 | 4.55e-10 | 4.55e-10
|  |  |  | k6 | -4.783e-09 | -4.186e-08 | -4.186e-08
|  |  |  | k7 | 1.962e-06 | 8.346e-07 | 8.346e-07
|  |  |  | k8 | -0.000229 | 5.482e-05 | 5.482e-05
|  |  |  | k9 | 0.003141 | -0.003191 | -0.003191
|  |  |  | k10 | 1.092 | 0.9729 | 0.9729
|  |  |  | k11 | 0 | 0 | 0
|  |  |  | k12 | -1.598 | -1.569 | -1.568
|  |  |  | k13 | 0.957 | 0.9778 | 0.99
Step 5: The Final values of incident energy can be found per 4.8
E1 | 22.8464 | J/cm2
E2 | 9.6129 | J/cm2
E3 | -60.3358 | J/cm2
E | 9.6129 | J/cm2 | 2.2975 | Cal/cm2
Step 6: The intermediate values of arc-flash boundary can be determined per 4.6
AFB at 0.6 | 1009.4289 | mm
AFB at 2.7 | 1286.5755 | mm
AFB at 14.3 | 1387.9443 | mm
Step 7: The final value of AFB can be determined per 4.8
AFB 1 | 2751.4933 | mm
AFB 2 | 1383.575 | mm
AFB 3 | -5846.8507 | mm
AFB | 1383.575 | mm
Step 8: To account for the arcing current variation use the equations in 4.4 to find the correction factor
VarCf | 0.023915 |  |  |  | Table-2
[5 empty] | K1 | 0
[5 empty] | K2 | -1.4269e-06
Correction factor | 0.98804 |  |  |  | K3 | 8.3137e-05
[5 empty] | K4 | -0.0019382
[5 empty] | K5 | 0.022366
[5 empty] | K6 | -0.12645
[5 empty] | K7 | 0.30226
Step 9: Adjust the intermediate values of arcing current using the correction factor
For 600 Volts | Iarc_600_min | 4.0952 | kA
For 2700 Volts | Iarc_2700_min | 5.0356 | kA
For 14300 Volts | Iarc_600_min | 5.502 | kA
Step 10: Find the reduced final arcing current per the equations and instructions provided in 4.8
Iarc_1 | 10.0067 | kA
Iarc_2 | 5.4819 | kA
Iarc_3 | -18.4348 | kA
Iarc | 5.4819 | kA
T | 252 | ms
Step 11: Repeat step 4 using the reduced intermediate currents
Table-3
[5 empty] | 0.6 kV | 2.7 kV | 14.3 kV
E at 0.6 | 4.2789 | J/cm2 |  | k1 | 0.75336 | 2.4002 | 3.8259
E at 2.7 | 6.3797 | J/cm2 |  | k2 | 0.566 | 0.165 | 0.11
E at 14.3 | 7.4437 | J/cm2 |  | k3 | 1.7526 | 0.3542 | -0.99975
|  |  |  | k4 | 0 | -1.557e-12 | -1.557e-12
|  |  |  | k5 | 0 | 4.55e-10 | 4.55e-10
|  |  |  | k6 | -4.783e-09 | -4.186e-08 | -4.186e-08
|  |  |  | k7 | 1.962e-06 | 8.346e-07 | 8.346e-07
|  |  |  | k8 | -0.000229 | 5.482e-05 | 5.482e-05
|  |  |  | k9 | 0.003141 | -0.003191 | -0.003191
|  |  |  | k10 | 1.092 | 0.9729 | 0.9729
|  |  |  | k11 | 0 | 0 | 0
|  |  |  | k12 | -1.598 | -1.569 | -1.568
|  |  |  | k13 | 0.957 | 0.9778 | 0.99
Step 12: Repeat step 5 using the reduced arcing currents
E1 | 17.4836 | J/cm2
E2 | 7.3978 | J/cm2
E3 | -45.9124 | J/cm2
E | 7.3978 | J/cm2 | 1.7681
Step 13: Repeat step 6 using the reduced arcing currents
AFB at 0.6 | 827.3405 | mm
AFB at 2.7 | 1065.2014 | mm
AFB at 14.3 | 1175.4897 | mm
Step 14: The final value of AFB can be determined per 4.8
AFB 1 | 2322.4662 | mm
AFB 2 | 1170.7359 | mm
AFB 3 | -4916.9814 | mm
AFB | 1170.7359 | mm

## LV - 2018
Step 1: Determine the intermediate arcing currents using the equations provided in section 4.3
Table-1
Arc Flash Calculation 1584 -2018 | [5 empty] | VCB
0.6 kV
Voltage | 0.42 | kV |  |  | K1 | -0.04287
Ibf | 48.11 | kA |  |  | K2 | 1.035
Gap B/w Conductors G | 32 | mm |  |  | K3 | -0.083
Working Distance | 609.6 | mm |  |  | K4 | 0
Enclose dimensions |  |  |  |  | K5 | 0
Width | 508 | mm | 508mm to 1244.6mm |  | K6 | -4.783e-09
Height | 508 | mm | 508mm to 1244.6mm |  | K7 | 1.962e-06
Depth | 508 | mm |  |  | K8 | -0.000229
[5 empty] | K9 | 0.003141
[5 empty] | K10 | 1.092
Iarc at 0.6 kV | 33.9165 | kA
Step 2: Find the final arcing current per 4.9
Final Iarc | 27.4779 | kA
FCT | 168 | ms
Step 3: Find the final arcing current per the equations and instructions provided in 4.7
Table-6
|  |  | Width< 508 (mm) | 508< Width< 660.4 (mm) | 660 < Width< 1244.6 (mm) | Width>1244.6 (mm)
Width 1 | 20 |  | 508 | 660.4 | 1244.6 | 1245
|  |  | 20 | 20 | 24.674 | 31.083
|  |  | Height< 508 (mm) | 508< Height< 660.4 (mm) | 660 < Height< 1244.6 (mm) | Height>1244.6 (mm)
Height 1 | 20 |  | 508 | 660.4 | 1244.6 | 1245
|  |  | 20 | 20 | 20 | 49
Table-7
ESS | 20 |  |  | B1 | B2 | B3
|  |  |  | -0.000302 | 0.03441 | 0.4325
Correction factor
CF | 0.9999
Step 4: The intermediate values of incident energy can be found per 4.5
Table-3
0.6 kV
E at 0.6 | 33.1779 | J/cm2 |  | k1 | 0.75336
|  |  |  | k2 | 0.566
| 7.9297 | cal/cm2 |  | k3 | 1.7526
|  |  |  | k4 | 0
|  |  |  | k5 | 0
|  |  |  | k6 | -4.783e-09
|  |  |  | k7 | 1.962e-06
|  |  |  | k8 | -0.000229
|  |  |  | k9 | 0.003141
|  |  |  | k10 | 1.092
|  |  |  | k11 | 0
|  |  |  | k12 | -1.598
|  |  |  | k13 | 0.957
Step 5: The Final values of incident energy can be found per 4.8
E1 | 33.1779 | J/cm2
| 7.9297 | cal/cm2
Step 6: The intermediate values of arc-flash boundary can be determined per 4.6
AFB at 0.6 | 1987.166 | mm
Step 7: The final value of AFB can be determined per 4.8
AFB 1 | 1987.166 | mm | 1.9872 | m
| 78.2349 | Inch
Step 8: To account for the arcing current variation use the equations in 4.4 to find the correction factor
VarCf | 0.25296 |  |  |  | Table-2
[5 empty] | K1 | 0
[5 empty] | K2 | -1.4269e-06
Correction factor | 0.87352 |  |  |  | K3 | 8.3137e-05
[5 empty] | K4 | -0.0019382
[5 empty] | K5 | 0.022366
[5 empty] | K6 | -0.12645
[5 empty] | K7 | 0.30226
Step 9: Adjust the intermediate values of arcing current using the correction factor
For 600 Volts | Iarc_600_min | 24.0026 | kA
| T | 200 | ms
Step 10: Repeat step 4 using the reduced intermediate currents
Table-3
0.6 kV
E at 0.6 | 34.7032 | J/cm2 |  | k1 | 0.75336
|  |  |  | k2 | 0.566
| 8.2943 | cal/cm2 |  | k3 | 1.7526
|  |  |  | k4 | 0
|  |  |  | k5 | 0
|  |  |  | k6 | -4.783e-09
|  |  |  | k7 | 1.962e-06
|  |  |  | k8 | -0.000229
|  |  |  | k9 | 0.003141
|  |  |  | k10 | 1.092
|  |  |  | k11 | 0
|  |  |  | k12 | -1.598
|  |  |  | k13 | 0.957
Step 11:The final value of incident energy can be determined per 4.9
E1 | 34.7032 | J/cm2
| 8.2943 | cal/cm2
Step 12: Repeat step 6 using the reduced arcing currents
AFB at 0.6 | 2043.8517 | mm
| 80.4666 | Inch
Step 13: The final value of AFB can be determined per 4.8
AFB 1 | 2043.8517 | mm
| 80.4666 | Inch

## 2002
S.No | SC, Ibf (kA) | K |  | V (kV) | Gap (G, mm) | Log (Ia) | Ia (kA) | 85% Ia (kA) | K1 | K2 |  | Log(En) | En (J/cm2) | Cf | Arc t (s) | D (mm) | x factor | E (J/cm2) | E, (cal/cm2) | DB (m)
1 | 45 | Box | -0.097 | 0.48 | 32 | 1.3432 | 22.0411 | 18.7349 | -0.555 | Grounded | -0.113 | 0.81924 | 6.5953 | 1.5 | 0.0613 | 609.6 | 1.473 | 12.699 | 3.0351 | 1.1478
2 | 45 | Box | -0.097 | 0.48 | 32 | 1.3432 | 22.0411 | 18.7349 | -0.555 | Grounded | -0.113 | 0.81924 | 6.5953 | 1.5 | 0.319 | 609.6 | 1.473 | 66.0843 | 15.7945 | 3.5169 | Open | Ungrounded/High R
[21 empty] | Box | Grounded
3250

## Sheet1
550
498
|  | 3500 | 4550
|  | 560 | 3360 | 4368
2782 | 3060.2
2225.6 | 2893.28