## Transmission line
transmission line calculations
voltage,v | 11 | KV
MVA | 100
R | 0.02312 | ohms/km
X | 0.33144 | ohms/km
Length | 1 | km
R | 0.02312 | ohms
X | 0.33144 | ohms
Zb | 1.21 | pu | base value | zb=(kvb)^2/MVAb
R | 0.019107
X | 0.27392
Rtl | 1.9107
Xtl | 27.3917
Rg | 0.0093488
Xg | 0.13088
Rt=Rg+R | 0.028456
Xt=Xg+X | 0.4048
Zt=sqrt(R^2+X^2)
Zt | 0.4058
If=Vpf/Zt |  | Vpf | 1
If | 2.4643
Ib=MVAb/sqrt(3)*v
Ib | 5.2486
Iactual | 12.9341

## Transformer calculations
transformer calculations
MVA | 100
V at HV side | 220 | kv
V at LV side | 33 | kv
full load current at HV side
HV FLA | (MVA*1000)/sqrt(3)*Vhv
262.4319
full load current at the LV side
LV FLA | (MVA*1000)/SQRT(3)*Vlv
1749.5463
Imp of T/F ZT | 10
Rest of T/F RT | 0.995
React of T/F XT | 9.95
To convert (%) to (pu) values
ZT | 0.1 | pu
RT | 0.00995 | pu
XT | 0.0995 | pu
Impedance correction factor as per IEC 60909
KT=0.95(Cmax/1+0.6*XT)
Cmax | 1.1 |  | 0.0597
KT | 0.98613 |  | 1.0597
impedance corretion factor with ZT,XT,RT
ZT*KT | 0.098613
RT*KT | 0.009812
XT*KT | 0.09812
For 220KV Rating Grid the R and X values are
RG | 0.00046744
XG | 0.0065441
ZT=SQRT(R)^2+(X)^2
RT=RG+(RT*KT)
XT=XG+(XT*KT)
RT | 0.010279 | ohms
XT | 0.10466 | ohms
ZT | 0.10517 | ohms
for 3ph fault currrent
assume ,Vpf | 1
If | 9.5086 | pu
Base value of current,Ib =MVAb/sqrt(3)*Vlv
Ib | 1.7495
pu=actual/base
actual=pu*base
Iactual | 16.6358 | kA

## C factor=1.1
transformer calculations
MVA | 100
V at HV side | 220 | kv
V at LV side | 33 | kv
full load current at HV side
HV FLA | (MVA*1000)/sqrt(3)*Vhv
262.4319
full load current at the LV side
LV FLA | (MVA*1000)/SQRT(3)*Vlv
1749.5463
Imp of T/F ZT | 10
Rest of T/F RT | 0.995
React of T/F XT | 9.95
To convert (%) to (pu) values
ZT | 0.1 | pu
RT | 0.00995 | pu
XT | 0.0995 | pu
Impedance correction factor as per IEC 60909
KT=0.95(Cmax/1+0.6*XT)
Cmax | 1.1 |  | 0.0597
KT | 0.98613 |  | 1.0597
impedance corretion factor with ZT,XT,RT
ZT*KT | 0.098613
RT*KT | 0.009812
XT*KT | 0.09812
For 220KV Rating Grid the R and X values are
RG | 0.00046744
XG | 0.0065441
By considering c factor =1.1
1.1
RT=1.1*RG+RT*XT
XT=1.1*XG+XT*KT
ZT=SQRT(R)^2+(X)^2
RT | 0.010326
XT | 0.10532
ZT | 0.10582
For 3ph fault current
assume Vpf=1
Vpf | 1
If=Vpf/ZT
If | 9.4497
base value of current,Ib=MVAb/sqrt(3)*Vlv
Ib | 1.7495 | KA
pu=actual/base
actual=pu*base
Iactual | 16.5327 | KA
for C factor =1.1
1.1
Iactual | 18.186 | KA

## Cable Calculations
[6 empty] | T | 20
Rref | 0.159 |  |  |  |  | Tref | 70
V | 11 | kv | 100 | MVA |  | alpha | 0.00393
R | 0.12776 | ohms/km |  |  | R=Rref(1+alpha(T-Tref))
X | 0.0962 | ohms/km
length | 1 | km |  |  |  | TRUE
R | 0.12776 | ohms | actual values
X | 0.0962 | ohms
Zb | 1.21 | base value | Zb=(KVb)^2/MVAb
R cable | 0.10558
X cable | 0.079504 |  | Rg | 0.0093488
|  |  | Xg | 0.13088
Rt=Rg+Rc | 0.11493
Xt=Xg+Xc | 0.21039
|  |  | Zt | sqrt(R)^2+(X)^2
Zt | 0.23973
|  |  | Vpf | 1
|  |  | If | Vpf/Zt
If | 4.1713
|  |  | Ib | MVAb/(sqrt(3)*V)
Ib | 5.2486
I actual | 21.8937

## Grid
MVAb | 100
Vl | 11 | kv | Vph=Vl/sqrt(3)
Vph | 6.3509 | kv
3ph Isc | 40 | kA | 1ph Isc | 40 | kA
3ph X/R | 14 |  | 1ph X/R | 14
MVA for 3ph | sqrt(3)*Vl*Isc
| 762.1024 | MVA
MVA for 1ph | Vph*Isc
| 254.0341 | MVA
Impedance value for 3ph
Z1=Vph/Isc
Z1 | 0.15877
X/R | 14
X | 0.15837
we know that Z=sqrt(R)^2+(X)^2
=R^2+(4R)^2
=R^2(1+(4)^2
Z | =sqrt(R)^2*(17)
=SQRT(17)*R
z | =14.0235673*R
R | Z/14.03566885
R | 0.011312
Impedance value for 1ph
Zo=(3Vph/Isc)-2Z1
Zo | 0.15877
Ro | 0.011312
Xo | 0.15837
Zb=(KVb)^2/MVAb
1.21
per unit values
Zpu | 0.13122
Rpu | 0.0093488
Xpu | 0.13088
for % values
Z% | 13.1216
R% | 0.93488
X% | 13.0883